## RECT PIPE DROP
INPUT
Riser Length, ft (inside) | 3
Riser Width, ft (inside) | 3
Barrel Diameter, in | 18
Manning's n-value | 0.025
Skew angle, degrees | 90 |  |  |  | Max. Tailwater, el. | 97
Upstream SS, #:1 | 2
Downstream SS, #:1 | 3
Top Width, ft | 10
Extra Pipe, ft | 5
Elevation
Top of Dam, el. | 102
Design High Water, el. | 101
Auxiliary Spillway, el. | 100
Riser Inlet, el. | 98
Barrel Inlet, invert, el. | 95
Barrel Outlet, invert, el. | 94.1
Toe of Dam, el. | 94
Pipe length, ft. | 47.0096
EQUATIONS
Elevation (ft) | Weir Flow (cfs) | High Orifice (cfs) | Low Orifice (cfs) | Pipe Flow (cfs) | Design Flow (cfs)
98 | 0 | 0 | 12.7631 | 6.2379 | 0
98.1 | 1.1764 | 13.7037 | 13.0437 | 6.5424 | 1.1764
98.2 | 3.3273 | 19.3799 | 13.3183 | 6.8333 | 3.3273
98.3 | 6.1126 | 23.7354 | 13.5874 | 7.1123 | 6.1126
98.4 | 9.4109 | 27.4073 | 13.8513 | 7.3808 | 7.3808
98.5 | 13.1522 | 30.6423 | 14.1102 | 7.6399 | 7.6399
98.6 | 17.289 | 33.567 | 14.3645 | 7.8904 | 7.8904
98.7 | 21.7866 | 36.2565 | 14.6143 | 8.1333 | 8.1333
98.8 | 26.6182 | 38.7598 | 14.8599 | 8.369 | 8.369
98.9 | 31.7619 | 41.111 | 15.1016 | 8.5984 | 8.5984
99 | 37.2 | 43.3348 | 15.3394 | 8.8217 | 8.8217
99.1 | 42.9173 | 45.4499 | 15.5736 | 9.0396 | 9.0396
99.2 | 48.9007 | 47.4709 | 15.8043 | 9.2523 | 9.2523
99.3 | 55.1389 | 49.4093 | 16.0317 | 9.4603 | 9.4603
99.4 | 61.6219 | 51.2744 | 16.256 | 9.6637 | 9.6637
99.5 | 68.3408 | 53.0741 | 16.4772 | 9.863 | 9.863
99.6 | 75.2875 | 54.8147 | 16.6954 | 10.0583 | 10.0583
99.7 | 82.4549 | 56.5017 | 16.9108 | 10.2499 | 10.2499
99.8 | 89.8363 | 58.1397 | 17.1236 | 10.438 | 10.438
99.9 | 97.4257 | 59.7329 | 17.3337 | 10.6228 | 10.6228
100 | 105.2175 | 61.2846 | 17.5413 | 10.8044 | 10.8044
100.1 | 113.2066 | 62.7981 | 17.7464 | 10.983 | 10.983
100.2 | 121.3883 | 64.2759 | 17.9493 | 11.1587 | 11.1587
100.3 | 129.7582 | 65.7205 | 18.1498 | 11.3317 | 11.3317
100.4 | 138.312 | 67.134 | 18.3482 | 11.5022 | 11.5022
100.5 | 147.0459 | 68.5183 | 18.5444 | 11.6701 | 11.6701
100.6 | 155.9563 | 69.8752 | 18.7386 | 11.8356 | 11.8356
100.7 | 165.0398 | 71.2063 | 18.9308 | 11.9989 | 11.9989
100.8 | 174.293 | 72.513 | 19.1211 | 12.1599 | 12.1599
100.9 | 183.713 | 73.7965 | 19.3095 | 12.3189 | 12.3189
101 | 193.2969 | 75.0581 | 19.496 | 12.4758 | 12.4758
Top of Dam, El.
Design High Water, El.
Riser, El.
Barrel Inlet, El.
Barrel Outlet, El.
Toe of Dam, El.
Auxiliary Spillway, El.

## CIRCULAR PIPE DROP
INPUT
Riser Diameter, in | 36
Barrel Diameter, in | 18
Manning's n-value | 0.025
Skew angle, degrees | 90
Upstream SS, #:1 | 2 |  |  |  | Max. Tailwater, el.
Downstream SS, #:1 | 3
Top width, ft | 10
Extra pipe, ft | 5
Elevation
Top of Dam, el. | 108
Design High Water, el. | 107
Auxiliary Spillway, el. | 106
Riser Inlet, el. | 98
Barrel Inlet, invert, el. | 95
Barrel Outlet, invert, el. | 94.1
Toe of Dam, el. | 94
Pipe length, ft. | 77.0056
EQUATIONS
Elevation (ft) | Weir Flow (cfs) | High Orifice (cfs) | Low Orifice (cfs) | Pipe Flow (cfs) | Design Flow (cfs)
98 | 0 | 0 | 12.9759 | 9.3866 | 0
98.1 | 0.99247 | 10.9422 | 13.2611 | 9.5344 | 0.99247
98.2 | 2.8071 | 15.4746 | 13.5403 | 9.68 | 2.8071
98.3 | 5.157 | 18.9525 | 13.8139 | 9.8234 | 5.157
98.4 | 7.9397 | 21.8844 | 14.0821 | 9.9647 | 7.9397
98.5 | 11.0961 | 24.4675 | 14.3454 | 10.1041 | 10.1041
98.6 | 14.5862 | 26.8028 | 14.6039 | 10.2416 | 10.2416
98.7 | 18.3807 | 28.9504 | 14.8579 | 10.3772 | 10.3772
98.8 | 22.4569 | 30.9493 | 15.1076 | 10.5111 | 10.5111
98.9 | 26.7966 | 32.8266 | 15.3533 | 10.6433 | 10.6433
99 | 31.3845 | 34.6023 | 15.5951 | 10.7739 | 10.7739
99.1 | 36.208 | 36.2912 | 15.8332 | 10.903 | 10.903
99.2 | 41.256 | 37.9049 | 16.0677 | 11.0305 | 11.0305
99.3 | 46.519 | 39.4527 | 16.2989 | 11.1566 | 11.1566
99.4 | 51.9885 | 40.942 | 16.5269 | 11.2812 | 11.2812
99.5 | 57.657 | 42.379 | 16.7518 | 11.4045 | 11.4045
99.6 | 63.5178 | 43.7689 | 16.9737 | 11.5265 | 11.5265
99.7 | 69.5647 | 45.1159 | 17.1927 | 11.6472 | 11.6472
99.8 | 75.7921 | 46.4239 | 17.409 | 11.7667 | 11.7667
99.9 | 82.1951 | 47.696 | 17.6226 | 11.8849 | 11.8849
100 | 88.7688 | 48.9351 | 17.8336 | 12.002 | 12.002
100.1 | 95.509 | 50.1435 | 18.0422 | 12.118 | 12.118
100.2 | 102.4117 | 51.3235 | 18.2484 | 12.2329 | 12.2329
100.3 | 109.473 | 52.477 | 18.4523 | 12.3466 | 12.3466
100.4 | 116.6896 | 53.6057 | 18.654 | 12.4594 | 12.4594
100.5 | 124.0582 | 54.7111 | 18.8535 | 12.5712 | 12.5712
100.6 | 131.5756 | 55.7946 | 19.0509 | 12.6819 | 12.6819
100.7 | 139.239 | 56.8574 | 19.2463 | 12.7917 | 12.7917
100.8 | 147.0457 | 57.9007 | 19.4398 | 12.9006 | 12.9006
100.9 | 154.9931 | 58.9256 | 19.6313 | 13.0085 | 13.0085
101 | 163.0787 | 59.933 | 19.821 | 13.1156 | 13.1156
101.1 | 171.3002 | 60.9237 | 20.0088 | 13.2218 | 13.2218
101.2 | 179.6554 | 61.8985 | 20.195 | 13.3272 | 13.3272
101.3 | 188.1422 | 62.8582 | 20.3794 | 13.4317 | 13.4317
101.4 | 196.7586 | 63.8035 | 20.5622 | 13.5354 | 13.5354
101.5 | 205.5027 | 64.735 | 20.7434 | 13.6383 | 13.6383
101.6 | 214.3725 | 65.6533 | 20.923 | 13.7405 | 13.7405
101.7 | 223.3665 | 66.5589 | 21.101 | 13.8419 | 13.8419
101.8 | 232.4828 | 67.4523 | 21.2776 | 13.9426 | 13.9426
101.9 | 241.7198 | 68.3341 | 21.4527 | 14.0425 | 14.0425
102 | 251.0761 | 69.2046 | 21.6264 | 14.1418 | 14.1418
102.1 | 260.55 | 70.0643 | 21.7988 | 14.2403 | 14.2403
102.2 | 270.1402 | 70.9136 | 21.9697 | 14.3382 | 14.3382
102.3 | 279.8453 | 71.7529 | 22.1394 | 14.4354 | 14.4354
102.4 | 289.6639 | 72.5824 | 22.3078 | 14.532 | 14.532
102.5 | 299.5947 | 73.4026 | 22.4749 | 14.6279 | 14.6279
102.6 | 309.6365 | 74.2137 | 22.6407 | 14.7232 | 14.7232
102.7 | 319.788 | 75.016 | 22.8054 | 14.8179 | 14.8179
102.8 | 330.0481 | 75.8099 | 22.9689 | 14.9119 | 14.9119
102.9 | 340.4156 | 76.5955 | 23.1312 | 15.0054 | 15.0054
103 | 350.8895 | 77.3731 | 23.2924 | 15.0984 | 15.0984
103.1 | 361.4686 | 78.143 | 23.4525 | 15.1907 | 15.1907
103.2 | 372.152 | 78.9054 | 23.6115 | 15.2825 | 15.2825
103.3 | 382.9386 | 79.6605 | 23.7694 | 15.3737 | 15.3737
103.4 | 393.8275 | 80.4085 | 23.9263 | 15.4644 | 15.4644
103.5 | 404.8176 | 81.1496 | 24.0822 | 15.5546 | 15.5546
103.6 | 415.9081 | 81.884 | 24.2371 | 15.6443 | 15.6443
103.7 | 427.0981 | 82.6119 | 24.391 | 15.7334 | 15.7334
103.8 | 438.3867 | 83.3334 | 24.5439 | 15.822 | 15.822
103.9 | 449.773 | 84.0487 | 24.6958 | 15.9102 | 15.9102
104 | 461.2562 | 84.758 | 24.8469 | 15.9978 | 15.9978
104.1 | 472.8355 | 85.4614 | 24.997 | 16.085 | 16.085
104.2 | 484.5102 | 86.1591 | 25.1463 | 16.1717 | 16.1717
104.3 | 496.2793 | 86.8511 | 25.2946 | 16.258 | 16.258
104.4 | 508.1423 | 87.5377 | 25.4421 | 16.3438 | 16.3438
104.5 | 520.0983 | 88.2189 | 25.5888 | 16.4291 | 16.4291
104.6 | 532.1466 | 88.895 | 25.7346 | 16.514 | 16.514
104.7 | 544.2865 | 89.5659 | 25.8795 | 16.5985 | 16.5985
104.8 | 556.5174 | 90.2318 | 26.0237 | 16.6825 | 16.6825
104.9 | 568.8385 | 90.8928 | 26.1671 | 16.7662 | 16.7662
105 | 581.2493 | 91.5491 | 26.3097 | 16.8494 | 16.8494
105.1 | 593.749 | 92.2007 | 26.4515 | 16.9322 | 16.9322
105.2 | 606.337 | 92.8478 | 26.5926 | 17.0146 | 17.0146
105.3 | 619.0128 | 93.4903 | 26.7329 | 17.0966 | 17.0966
105.4 | 631.7757 | 94.1285 | 26.8725 | 17.1782 | 17.1782
105.5 | 644.6252 | 94.7623 | 27.0114 | 17.2594 | 17.2594
105.6 | 657.5605 | 95.392 | 27.1496 | 17.3402 | 17.3402
105.7 | 670.5813 | 96.0175 | 27.2871 | 17.4207 | 17.4207
105.8 | 683.6869 | 96.639 | 27.4238 | 17.5008 | 17.5008
105.9 | 696.8768 | 97.2565 | 27.5599 | 17.5805 | 17.5805
106 | 710.1504 | 97.8701 | 27.6954 | 17.6599 | 17.6599
106.1 | 723.5073 | 98.4799 | 27.8301 | 17.7389 | 17.7389
106.2 | 736.9468 | 99.086 | 27.9643 | 17.8176 | 17.8176
106.3 | 750.4686 | 99.6883 | 28.0977 | 17.8959 | 17.8959
106.4 | 764.072 | 100.287 | 28.2306 | 17.9739 | 17.9739
106.5 | 777.7567 | 100.8822 | 28.3628 | 18.0515 | 18.0515
106.6 | 791.5221 | 101.4739 | 28.4944 | 18.1288 | 18.1288
106.7 | 805.3678 | 102.0622 | 28.6254 | 18.2058 | 18.2058
106.8 | 819.2932 | 102.6471 | 28.7559 | 18.2825 | 18.2825
106.9 | 833.2981 | 103.2286 | 28.8857 | 18.3588 | 18.3588
107 | 847.3818 | 103.8069 | 29.0149 | 18.4348 | 18.4348
Top of Dam, El.
Auxiliary Spillway, El.
Riser, El.
Barrel Inlet, El.
Barrel Outlet, El.
Toe of Dam, El.
Design High Water, El.

## REFERENCES
*for Rectangular riser/barrel - use vertical distance from water surface elevation to the tailwater elevation or minumum tailwater elevation at 0.6 pipe diameters above the pipe outlet