NATURAL RESOURCES CONSERVATION SERVICE

CONSTRUCTION SPECIFICTION

North Dakota

PLASTIC PIPELINES AND CONDUITS

(Code 430)

# SCOPE

The work shall consist of furnishing and installing plastic pipe or conduit complete with appurtenances and fittings as shown on the drawings.

# MATERIALS

Pipe—The pipe shall be as uniform as commercially practicable in color, opaqueness, density, and other specified physical properties. It shall be free from visible cracks, holes, foreign inclusions, or other defects. The dimensions of the pipe shall be measured as prescribed in ASTM D 2122.  Unless otherwise specified, the pipe shall conform to the requirements listed in this specification and the applicable reference specifications in table 547–2, and as specified is Section 12 of this speciation, and the requirements shown on the drawings.

## Table 547–2 Pipe Specification - Poly vinyl chloride (PVC) pipe

Plastic pipe - Schedules 40, 80, 120	ASTM D 1785

ASTM D 2466

Pressure rated pipe - SDR Series	AWWA C 900

ASTM D 2241

Plastic drain, waste, and vent pipe and fittings	ASTM D 2665

Joints for IPS PVC pipe using solvent weld cement	ASTM D 2672

Composite sewer pipe	ASTM D 2680

Type PSM PVC sewer pipe and fittings	ASTM D 3034

Large-diameter gravity sewer pipe and fittings	ASTM F 679

Smooth-Wall Underdrain Systems for

Highway, Airport, and Similar Drainage	ASTM F 758

Profile gravity sewer pipe and fittings

based on controlled inside diameter	ASTM F 794

Corrugated sewer pipe with a smooth interior and fittings	ASTM F 949

Pressure pipe, 4-inch through 12-inch for water distribution	AWWA C 900

Water transmission pipe, nominal

diameters 14-inch through 36-inch	AWWA C 905

### Polyethylene (PE) plastic pipe

Schedule 40	ASTM D 2104

12 to 60-in annular corrugated profile-wall

polyethylene (PE) pipe and fittings	ASTM F 2306

SIDR-PR based on controlled inside diameter	ASTM D 2239

Schedules 40 and 80 Based on outside diameter	ASTM D 2447

SDR-PR based on controlled outside diameter	ASTM D 3035

### High density polyethylene (HDPE) plastic pipe

Plastic pipe and fittings	ASTM D 3350

SDR-PR based on controlled outside diameter	ASTM F 714

Heat joining polyolefin pipe and fittings	ASTM D 2657

### Acrylonitrile-butadiene-styrene (ABS) pipe

Plastic pipe, schedules 40 and 80	ASTM D 1527

Composite sewer pipe	ASTM D 2680

Fittings and joints—Fittings and joints shall be of a schedule, SDR or DR, pressure class, external load carrying capacity, or pipe stiffness that equals or exceeds that of the plastic pipe. The dimensions of fittings and joints shall be compatible with the pipe and measured in accordance with ASTM D 2122. Joint and fitting material shall be compatible with the pipe material. The joints and fittings shall be as uniform as commercially practicable in color, opaqueness, density, and other specified physical properties. It shall be free from visible cracks, holes, foreign inclusions, or other defects. Fittings and joints shall conform to the requirements listed in this specification, the requirements of the applicable specification referenced in the ASTM or AWWA specification for the pipe, and the requirements shown on the drawings.

Valves – All valve types shall be constructed of materials suitable for the for the environmental exposure and installation.  Size, pressure rating, and type of valves shall meet the requirements as described in the construction details and drawings.

Valve risers or manholes shall be as shown on the drawings and be constructed in such a manner that they will be resistant to damage or deterioration caused by the elements, leaking water, vandals, equipment or other hazards.

A pressure relief valve is a type of safety valve used to control or limit the pressure in a system.  The relief valve is designed to open at a predetermined set pressure. If the set pressure is exceeded, the valve is forced open, releasing fluid and pressure until the pressure drops below the set pressure of the valve.

Air and vacuum valve types are defined as follows and shall be of the size, type, and pressure rating specified on the drawings:

Air-Release Valve (1-way valve)

A continuous acting valve that has a small venting orifice, generally ranging between 1/16 and 3/8 inch in size. This valve releases air from the pipeline once the line is filled and under working pressure.  Examples of these valves would include the Valmatic 15-38-S.

Air-and-Vacuum Relief Valve (2-way valve)

A large venting orifice which exhausts large quantities of air during filling operations and allows air to re-enter the line to prevent vacuum buildup during emptying. It is not continuous acting since air cannot escape once water enters the valve.  Examples of these valves would include Waterman AV-150, Fresno 3000, and Valmatic 100-S.

Combination Air-Vacuum Relief and Air Release Valve (3-way valve)

Combines the functions of air-release and air-and-vacuum valves.  Examples of these valves would include Nelson ACV200, Waterman CR-101, Fresno 3500, and Valmatic 200C-S.

Combination Air-Vacuum Relief and Pressure Relief Valve (tri-action valve)

Combines the functions of pressure relief and air-and-vacuum valves.  Examples of these valves would include Hydro Engineering Tri-Action Valve.

Solvents—Solvents for solvent welded pipe joints shall be compatible with the plastic pipe used and shall conform to the requirements of the applicable specification referenced in the ASTM or AWWA specification for the pipe, fitting, or joint.

Gaskets—Rubber gaskets for pipe joints shall conform to the requirements of ASTM F 477, Elastomeric Seals (Gaskets) for Jointing Plastic Pipe.

# HANDLING THE PIPE

Pipe shall be delivered to the job site and handled by means that provide adequate support to the pipe and do not subject it to undue stresses or damage. When handling and placing plastic pipe, care shall be taken to prevent impact blows, abrasion damage, and gouging or cutting (by metal edges and/or surface or rocks). The manufacturer's special handling requirements shall be strictly observed. Special care shall be taken to avoid impact when the pipe must be handled at a temperature of 40 degrees Fahrenheit or less.

Pipe shall be stored on a relatively flat surface so that the barrels are evenly supported. Unless the pipe is specifically manufactured to withstand exposure to ultraviolet radiation, it shall be covered with an opaque material when stored outdoors for 15 days or longer.

# JOINTS

Unless otherwise specified in Section 12 of this specification or shown on the drawings, joints shall be either bell or spigot type with elastomeric gaskets, coupling type, solvent cement bell and spigot, or jointed by butt heat fusion. When a lubricant is required to facilitate joint assembly, it shall be a type having no deleterious effect on the gasket or pipe material.

Pipe joints shall be watertight at the pressures specified except where unsealed joints are indicated.

Pipe shall be installed and joined in accordance with the manufacturer's recommendations. Laying deflections and joint fitting or stab depths shall be within the manufacturer's recommended tolerances.

Flanged, banded, heat-fusion, or elastomeric-sealed mechanical joints shall be used when joining polyethylene (PE) and high density polyethylene (HDPE) pipe and fittings unless otherwise specified in Section 12 of this specification or as shown on the drawings.

Pipe ends shall be cut square and be deburred to provide a uniform, smooth surface for the jointing process. Reference marks shall be placed on the spigot ends to assist in determining when proper seating depth has been achieved within the joint.

# FITTINGS

Unless otherwise specified, steel fittings, valves, and bolted connections shall be painted or coated as recommended by the manufacturer.

Fittings for non-pressure pipe shall be of the same or similar material as the pipe and shall provide the same durability, watertightness, and strength as the pipe unless otherwise specified.

# EXCAVATION

Excavation shall be in accordance with Construction Specification 104, Excavation, and Section 12 of this specification or as shown on the drawings.

The pipe foundation shall be excavated a minimum of 4 inches lower than the pipe grade shown on the drawings or staked in the field whenever bedrock, boulders, cobbles, or other material that may cause pipe damage is encountered at planned pipe grade.

# LAYING AND BEDDING

The pipe shall be placed with care to prevent scratching of the pipe surface.  Pipe with scratches or gouges (penetration of more than 10 percent of wall thickness) shall be rejected.  The pipe conduits complete with fittings and other related appurtenances shall be installed to the line and grade shown on the drawings. The pipe shall be installed so that there is no reversal of grade between joints unless otherwise shown on the drawings.  It shall be firmly and uniformly bedded throughout its entire length by shaping the subgrade to conform to the conduit shape through the lower one-third of its circumference.  Blocking or mounding shall not be used to bring the pipe to final grade.

Bell-holes shall be made in the bedding under bells or couplings and other fittings to prevent pipe from being supported only by fittings.

When the pipe is bedded on an earthen subgrade, the subgrade shall be free from rocks, clods, or other sharp-edged objects.  If sand is used for the bedding material, the details shall be as shown on the drawings.

Just before placement, each pipe section shall be inspected to ensure that all foreign material is removed from inside the pipe. The pipe ends and the couplings shall be free of foreign material when assembled. At the completion of a work shift, all open ends of the pipeline shall be temporarily closed off using a suitable cover or plug.

Care shall be taken to prevent distortion and damage during hot or cold weather. During unusually hot weather (daytime high temperature of more than 90 degrees Fahrenheit), the pipe assembled in the trench shall be lightly backfilled or shaded to keep it as near to ground temperature as possible until final backfill is placed. Backfill operations should be performed during daily construction periods when the ground temperature and the temperature of the pipe do not vary more than 40 degrees Fahrenheit.

During installation, the pipe shall be firmly and uniformly bedded throughout its entire length, to the depth and in the manner specified in Section 12 of this specification or as shown on the drawings. Bell-holes shall be placed in bedding material under bells, couplings, and other fittings to assure the pipe is uniformly supported throughout its entire length. Blocking or mounding beneath the pipe to bring the pipe to final grade is not permitted.

# Pipe embedment

Earth bedding. The pipe shall be firmly and uniformly placed on compacted earthfill bedding or an in-place earth material bedding of ample bearing strength to support the pipe without noticeable settlement. The earth material on which the pipe is placed shall be of uniform density to prevent differential settlement.

Unless otherwise specified, a groove that closely conforms to the outside surface of the pipe shall be formed in the bedding. The depth of the groove shall be equal to or greater than 0.3 of the pipe diameter.

Earth bedding shall be compacted to a density not less than adjacent undisturbed in-place earth material or be compacted earth backfill. Earthfill material used for compacted earth bedding shall be free of rocks or stones greater than 1 inch in diameter and earth clods greater than 2 inches in diameter. The pipe shall be loaded sufficiently during the compaction of bedding under the haunches and around the sides of the pipe to prevent displacement from its final approved placement.

Sand, gravel, or crushed rock bedding. When sand, gravel, or crushed rock bedding is specified, the pipe shall be firmly and uniformly placed on the bedding material. Material for bedding shall not exceed 1 inch in diameter. Unless otherwise specified in Section 12 of this specification or shown on the drawings, the coarse-grained bedding material shall be carefully placed and compacted to a depth equal to or greater than 0.3 of the diameter of the pipe above the bottom of the pipe. The pipe shall be loaded sufficiently during backfilling and compaction around the sides to prevent displacement of the pipe from its final approved placement.

Pipe encased in drainfill. The pipe shall be firmly and uniformly placed on bedding of specified drainfill. Drainfill shall be placed and compacted as specified in Section 12 of this specification or as shown on the drawings to form a continuous uniform support around the entire circumference of the pipe. The pipe shall be loaded sufficiently during backfilling around the sides and during compaction to prevent displacement of the pipe.

# BACKFILLING

Prior to backfilling, the pipe shall be allowed to come to within a few degrees of the temperature that it will have after complete covering.  Special care shall be taken during initial backfill so that the pipe will not be displaced, nor will the grade or alignment be disturbed.  The pipe shall be tied down or loaded sufficiently during backfilling around the side to prevent its being lifted from the bedding.

The backfill material shall be carefully selected soil or sand, free from rocks and stones.  At the time of placement, the backfill material shall have sufficient moisture content so that the required degree of compaction can be obtained.

Backfill around the pipe shall be placed in layers not more than 4 inches thick before compaction.  Each layer of backfill shall be compacted with power tampers, hand tampers, or plate vibrators to the same density requirements as specified for the adjacent embankment.  Backfill over and around the pipe shall be brought up uniformly on all sides to provide adequate lateral support to the pipe.  The backfill shall extend a minimum of 2 feet over the pipe before earth embankment with earth moving equipment over the pipe is started.

All special backfilling requirements of the pipe manufacturer shall be met.

If sand is used for the backfill material around the pipe, the backfilling details shall be as shown on the drawings.

# THRUST BLOCKS AND ANCHORS

When specified, concrete thrust blocks and anchors shall be installed as shown on the drawings or specified in Section 12 of this specification.

The concrete for the thrust blocks and anchors shall be Class 3000M concrete unless otherwise specified in Section 12 of this specification and as shown on the drawings.

The thrust block cavity shall be hand dug into undisturbed soil or previously placed compacted backfill. The cavity shall be formed with soil or wood to hold the freshly placed concrete without displacement until an initial set has occurred.

When excavation beyond the designated trench widths and depths as shown on the drawings or specified in Section 12 of this specification occurs at locations where installation of concrete thrust blocks is required, the contractor shall install an alternative thrust block provision. The concrete thrust block shall have a thickness of one pipe diameter and a contact face area that shall be formed against the pipe as shown on the drawings or specified in Section 12 of this specification. Backfill shall be placed on all sides of the thrust block and to the sides of the excavation. It shall be compacted as specified for initial backfill.

# PRESSURE TESTING

When specified, the conduit shall be tested for leaks in the following manner or a manner approved by the engineer:

- Before pressure testing:

- Joints of the assembled pipeline shall be allowed to cure as recommended by the manufacturer.

- Pipeline shall be flushed and cleaned.

- All concrete anchors and thrust blocks shall be in place and allowed to cure for at least 3 days.

- Earth backfill shall be sufficient to anchor the conduit against movement during the pressure testing and compacted as specified in Sections 9 and 12 of this specification or as shown on the drawings.

- The conduit shall be braced and/or anchored at each end to prevent all potential pipe movement.

- The ends of the conduit shall be plugged.  The upstream plug shall have a standpipe installed vertically having a minimal diameter of 2 inches and shall be equipped with a shutoff valve.  All high points in the line shall be vented to evacuate air pockets.  The conduit and standpipe shall be slowly filled with water such that no air is entrapped during the filling operation.  After filling is complete, all vents shall be closed.

- During pressure testing, the water level in the standpipe shall be continuously maintained at a minimum of 10 feet above the highest invert elevation of the conduit for no less than 2 hours unless otherwise specified in Section 12 of this specification or as shown on the drawings.

The volume of water leakage in the 2-hour test period shall be recorded.  The maximum allowable leakage (L) in gallons per hour shall not exceed 0.02 time the nominal pipe diameter (D) in inches for each 1,000 feet of pipe, which is about 50 pipe joints (L=0.02 x D)

- When observed leakage exceeds the allowable, leaks shall be sealed by replacement of pipe and fittings as necessary.  The conduit shall be retested as described above.  The procedure shall be repeated until the conduit leakage does not exceed the allowable specified above/.

The contractor shall be fully responsible for any and all work required to correct leakage exceeding the amount specified.

# ITEMS OF WORK AND CONSTRUCTION DETAILS